## Sheet1
Compressed Guid | Component Id | Failure Id | Failure Mode | Failure Cause | Failure Effect | Severity | Occurrence | Detection
2vtK3jGx157BtoTg_RUTO0 | 1-5XV1 | F1.1 | damper stuck (closed) | actuator not operating or control not received | system failure or high energy consumption | 3 | 3 | 2
2vtK3jGx157BtoTg_RUTO0 | 1-5XV1 | F1.2 | damper stuck (open) | actuator not operating or control not received | faster filter's degradation or freezing coil in winter | 2 | 3 | 3
2zYtj8uzP1aBc9B80gppQx | 1-5FR1 | F2.1 | filter fouling | accumulating dirt | high energy consumption | 2 | 2 | 4
2zYtj8uzP1aBc9B80gppQx | 1-5FR1 | F2.2 | filter breakage | damaged filter | System failure | 4 | 2 | 4
1wbSO9wmL6JxyVV1JV_3Jq | 1-5WS1 | F3.1 | drive belt failure | belt broken | high energy consumption | 2 | 3 | 2
1wbSO9wmL6JxyVV1JV_3Jq | 1-5WS1 | F3.2 | wheel not operating | motor failure | high energy consumption | 3 | 2 | 2
1wbSO9wmL6JxyVV1JV_3Jt | 1-5CL1 | F4.1 | coil fouling | accumulated fine particles | reduced efficiency | 2 | 1 | 3
1wbSO9wmL6JxyVV1JV_3Jt | 1-5CL1 | F4.2 | coil not heating | failure in the system (valve/pump) providing heat | failure of requirement for thermal comfort | 3 | 3 | 4
1wbSO9wmL6JxyVV1JV_3Jo | 1-5WS1 | F5.1 | impeller wearing off | chemical corrosion | System failure | 3 | 1 | 4
1wbSO9wmL6JxyVV1JV_3Jo | 1-5WS1 | F5.2 | fan not operating | motor breakage | System failure | 4 | 3 | 2